## Slide 2
ROTEX HPSU compact V5
DAIKIN Altherma with integrated solar unit

## Slide 3
System build up
Equipment selection
System operation
Commissioning
Troubleshooting
What should have been said
Overview

## Slide 4
1. System build up
DAIKIN Altherma with integrated solar unit

## Slide 5
System build up
Indoor unit
Outdoor unit
Accessories/options
1.

## Slide 6
Indoor unit
1.1
3xx 5xx
Indoor unit
Notes: 300l tank not DHW
500l tank not DHW

## Slide 7
E HS (X/H) (B) 04 P 30 B
Indoor unit
1.1
Capacity 4/6/8/11/14/16kW
Tank size 300/500l
X = Heating/Cooling H = Heating only
European model
Hydrobox Solar
Bivalent heatexchanger
Material of the tank (Plastic)
Series
Notes: Heating only for Belgium (law)

## Slide 8
Indoor unit
1.1
New style and new hydraulics
Notes: Details later

## Slide 9
Indoor unit
1.1
New top cover
Notes: No screws
Easy to mount and unmount

## Slide 10
System build up
Outdoor unit
1.2
GBS GQI
4/6/8 kW 11/14/16kW
Notes: Like in the previouse versions

## Slide 11
Outdoor unit
1.2
E R L/H Q 0-- CA V3
Capacity 4/6/8/11/14/16kW
European model
Ambient zone L(cold) / H(mild)
Volatge supply
Version
Refrigernat R410
Outdoor unit
Notes: Like in the previouse versions

## Slide 12
Accessories/options: Outdoor unit
1.3
EKDP008CA drainpan (Small OU (04-08kW))
EKDPH008CA drainpan heater (Small OU (04-08kW))
EKFT008CA U-beams for mounting (Small OU (04-08kW) only)
EKHBPHTH16A bottom plate heater (for ERHQ)
EKDK04* drain plug (for ERHQ)
EK016SNC snow hood (for ERLQ - Big OU (11-16kW))

## Slide 13
Accessories/options: Outdoor unit
1.3
EKDP008CA drainpan (only for Small OU (04-08kW)
  Small OU (04-08 kW) for HPSU has free hanging coil
  If required, you can mount a drain pan for outdoor unit
  Collect water from defrost cycle and drain via central hole
  Consists of a drain pan and U-beams
Notes: The new outdoor has a free hanging coil so no drainpan. If drainpan is required, order this option.
Dimensions are in a way that ice cannot accumulate. When ordering the drainpan and when used in areas where ambient temperatures might go below 0°C, also heater is required (EKDPH) otherwise the drainhole might freeze.

## Slide 14
Accessories/options: Outdoor unit
1.3
2) EKDPH008CA drain pan heater (Small OU (04-08kW))
  Drain pan heater for drain pan EKDP008CA
  Recommended when a drain pan is used in cold regions
  90W & controlled by OU (faston terminal on pcb)
3) EKFT008CA U-beams (Small OU (04-08kW) only)
  U-beams for mounting outdoor unit without drainpan
  Height 25cm
Notes: Heater control: Heater is permanent ON when T is below 0°C. When ambient is above 0°C, the heater is only ON during defrost.
EKFT: use this instead of higher blocks. EKFT is sized so that it perfectly fits under the unit to avoid ice accumulation starting from the casing & installation feet.

## Slide 15
Accessories/options: Outdoor unit
1.3
4) EKHBPHTH16A bottom plate heater (for ERHQ)
  Bottom plate heater for ERHQ* units
  Controlled by indoor unit (settings)
  EKRP1HBAA is also required (for control signal)
 |  | Bottom plate heater | Drain socket
 | ERLQ | Standard | Use prohibited
 | ERHQ | Optional kit (a) | Optional kit (a)
 | (a) Combination of both options prohibited |  | 
Notes: ATTENTION!!!! ERLQ has standard heater mounted.
If heater is required for ERHQ, then order EKHBPHTH16A.
If this heater is installed, following settings must be done:
A.2.2.6.4. Bottom plate heater connected to indoor unit: 0 = no, 1 = yes
F-02: bottom plate heater ON temperature (3~10°C)
F-03: bottom plate hysteresis: (2~5°C)

## Slide 16
Accessories/options: Outdoor unit
1.3
5) EKDK04* drain plug
(for ERHQ only, ERLQ has standard BPH for Small OU (04-08kW))
  Drain plug/stop kit
  To guide the condensate through one hole in the bottom plate
  Not allowed to use if bottom plate heater installed

## Slide 17
Accessories/options: Outdoor unit
1.3
6) EK016SNC snow hood (for ERLQ Big OU (11-16kW))
  Snow cover
  For low ambient/heavy snowfall
60
70
10
Notes: On the new small outdoor unit , the topplate is already shaped like a small snowcover.
For big outdoor ERLQ, this option EK016SNC can be used.
However, in areas where there is heavy snowfall, it is advised to build a small shed or at least a roof around the unit.

## Slide 18
Accessories/options: Indoor unit
1.3
RoCon OT1 additional ambient sensor (15 60 70 )
RoCon U1 room controller (15 70 34)
RoCon M1 mixer module (15 70 68)
RoCon G1 Gateway (15 70 56)
BU9c Backup heater (14 10 28)
SAA1 Boiler incorporation A1 ( 16 01 25)
SAK2 Storage tank incorporation heat exchanger version 2 (16 01 30)
SKB Convection brake (16 50 70)
HWC Hydraulic diverter DN 125 (17 29 00)
MK1/2 Mixer group (fittings) (15 60 67/72)
SAS1/2 Sludge and magnetite separator ( 15 60 21/23)
EFWXV15/20AVEB HP convector (14 20 10/11)
EKSRDS2A Solaris pressurized solar regulator
EKRPS4 regulation and pump unit

## Slide 19
Accessories/options: Indoor unit
1.3
RoCon aditional ambient sensor
  Better LWT calculation
  No influence of the OU
  Sensor of OU still available
RoCon additional U1 room controller
  no room thermostat it‘s a sensor
  can be used as remote controlle or Terminal
  Assignment to mixer module or living room
Notes: Aktivieren oder deaktivier bei defekt
Beschattetes/nicht beschattetes gerät

## Slide 20
Title - Top secret/Secret/Internal use only/Public
20
Accessories/options: Indoor unit
1.3
3) RoCon M1 mixer module
  Can be used as stand-alone solution or integrated via bus
  Specific training of operation and set up is on the Extranet
4) RoCon G1 Gateway inlc. ROTEX Control
  For Android and IOS
  Direct access to the B1 (CUI) for all RoCon units (A1/GCU and HPSU)
  Control of direct circuit, temperatures, time schedule and operation mode
  Displays system status, ambient and system temperatures
  Big Focus on safety therefore a direct internet connection should be used
  Specific training can be found on the Extranet
Notes: M1 only with B1 or CUI

## Slide 21
Title - Top secret/Secret/Internal use only/Public
21
Accessories/options: Indoor unit
1.3
6) SAA1 Boiler incorporation A1
  Connection for A1 bivalent operation with the HPSU
  Incl. pipe and fittings
  Unpressurised mode
5) BU9c Backup heater
  Additional heating for HPSU
  3 x 230V – 50 Hz / 9000 Watt
  Use as backup – and booster heater
  !1,2m long!
Notes: Also available as 3kw heater

## Slide 22
Title - Top secret/Secret/Internal use only/Public
22
Accessories/options: Indoor unit
1.3
7) SAK2 Storage tank incorporation heat exchanger V2
  Connection for secondary heat generator or ROTEX storage tank (2013 and newer)
  If using 3rd party ROTEX Solaris PHE is needed (6kW)
  Incl. pipe, fittings and pump
  Unpressurised mode
8) SKB Convection break
  To prevent circulation due to gravitiy
  Not for pressurised solar
  Max 95°C
Notes: Same as sas1 without pump

## Slide 23
Title - Top secret/Secret/Internal use only/Public
23
Accessories/options: Indoor unit
1.3
9) HWC Hydraulic diverter + WHWC Isolation
  For 4 zones
  Floor standing and with a high of 1,5 m
  Integrated separator discs
Notes: Flow rate
Necessary in Germany if you want money from the goverment.
Vorteile:- Hydraulische Entkopplung bei unterschiedlichen Volumenströmen - Kesselkreis bzw. Wärmeerzeugerkreis verfügt immer über eine konstante Durchflussmenge - Sanfte Regelung (hoher Wirkungsgrad, geringste Emissionen) - Hohe Leistungsspitzen der Verbraucher möglich - Geringer Aufwand für Regelung, preiswerte Lösung - als Entschlammungsbehälter einsetzbar (Entschlammungsstutzen notwendig) - als Luftabscheider einsetzbar (Entlüfungsventil gut zugänglich montieren, evtl. nach unten ziehen)

## Slide 24
Title - Top secret/Secret/Internal use only/Public
24
Accessories/options: Indoor unit
1.3
10) MK1/2 mixer groupe
  For mixed circuits
  Can be controlled of M1
  Fittings, if needed have to ordered seperately (VKM1)
  MK1 pressure contoled high-efficiency pump
  MK2 PWM-controlled high-efficiency pump
Notes: Via can bus connection to the U1 or B1

## Slide 25
Title - Top secret/Secret/Internal use only/Public
25
Accessories/options: Indoor unit
1.3
11) SAS1/2 Sludge and magnetite separator
  also vertical available
  1” connection
12) EFWXV15/20AVEB HP convector
  1,5 / 2kW available
  Constant comfort throughout the room
  Energy efficient heating and cooling system
  Optimum energy efficiency
  Reduced running costs
Notes: Show example
Convectors max 3

## Slide 26
Title - Top secret/Secret/Internal use only/Public
26
Accessories/options: Indoor unit
1.3
13) EKSRDS2A Solaris pressurized solar regulator
  For pressurized solar
  Depending on the connected thermistors… the controller finds the scheme
14) EKSRPS regulation and pump unit
  For Drain-Back-Solar / and pressurised
  Only one high efficient pump
  Up to 12 m
  Directly to the unit or separate possible

## Slide 27
2. Equipment selection
DAIKIN Altherma with integrated solar unit

## Slide 28
Title - Top secret/Secret/Internal use only/Public
28
Equipment selection
2.
Specs. Indoor
  3XX
  5XX
Specs. Outdoor
Electrical data Sheet

## Slide 29
Title - Top secret/Secret/Internal use only/Public
29
Specs. Indoor 3XX
2.1.1
Notes: 595 breit und 615 tief

## Slide 30
Title - Top secret/Secret/Internal use only/Public
30
Specs. Indoor 3XX
2.1.1
1905

## Slide 31
Title - Top secret/Secret/Internal use only/Public
31
Specs. Indoor 3XX
2.1.1
Notes: Only 27,8 l of fresh water easy to flush no stagnation
12l/m with 153L 40°C maximum showwering time of 13min
300 not for raindance (15-28l/min) bathtube or more than one bathroom
Our tank just reduced the temperature after tapping „normal“ tank if they get tapped empty they are emty

## Slide 32
Title - Top secret/Secret/Internal use only/Public
32
Specs. Indoor 3XX
2.1.1

## Slide 33
Title - Top secret/Secret/Internal use only/Public
33
Specs. Indoor 5XX
2.1.2
Notes: 790 cm breit und tief

## Slide 34
Title - Top secret/Secret/Internal use only/Public
34
Specs. Indoor 5XX
2.1.2
1905
Notes: 2 people to carry
(or one italien guy)

## Slide 35
Title - Top secret/Secret/Internal use only/Public
35
Specs. Indoor 5XX
2.1.2
Notes: 3) Storage tank charged just by heat pump without backup heater.
20min showering with 12l/m

## Slide 36
Title - Top secret/Secret/Internal use only/Public
36
Specs. Indoor 5XX
2.1.2

## Slide 37
Title - Top secret/Secret/Internal use only/Public
37
Specs. Outdoor
2.2.

## Slide 38
Title - Top secret/Secret/Internal use only/Public
38
Specs. Outdoor
2.2
20

## Slide 39
Title - Top secret/Secret/Internal use only/Public
39
Specs. Outdoor
2.2.
-25

## Slide 40
Title - Top secret/Secret/Internal use only/Public
40
Specs. Outdoor
2.2.

## Slide 41
Title - Top secret/Secret/Internal use only/Public
41
Specs. Outdoor
2.2.

## Slide 42
Title - Top secret/Secret/Internal use only/Public
42
Electrical data sheet
2.3.

## Slide 43
Title - Top secret/Secret/Internal use only/Public
43
Electrical data sheet
2.3.

## Slide 44
3. System operation
DAIKIN Altherma with integrated solar unit

## Slide 45
Title - Top secret/Secret/Internal use only/Public
45
System operation (only Indoor)
3.
Hydraulic
Electronic
Parameter

## Slide 46
Hydraulic
3.1.
Basis for highest heat pump efficiency
  Allows hygienic DHW preparation at low tank temperatures (50°C)
  No stagnation
  Very low standby losses (1.4 kWh per day)
  Multiple heat sources connectable (e.g. solar energy)
  No need for DHW expansion vessel, no spilling of heated DHW through the overpressure valve
  Lime scale don’t block the heat exchanger in normal operation
Security for the end user
  Always fresh water, since DHW prepared on demand
  No maintenance
  No sedimentation inside tank
Notes: Draw OLD round (inside) unit and new more edgi unit on the board
Draw limescale in the lowes cruit of the heatexchanger (if not flashed out can block)
Approx 6 cm isolation in HPSU 1-3
Approx 6,5-7 cam isolation in HPSU 4-5
Regulations have changed therefore the tank was optomized,
Harder test condition same result!
Isolation came bigger but tank couldn‘t come bigger so some small internal changes to keep the volume

## Slide 47
3.1.
304/308 EHSH(X)04P30A
304/308 BIV
EHSH(X)B04P30A
Cold water in
DHW out
Tank loading flow
Tank loading return
Bivalent flow
Bivalent return
Drain-Back flow
Drain-Back return
12 3 4 7 8
12 3 4567 8
Hydraulic
Notes: 300 units only have a drain back pipe due to space

## Slide 48
3.1.
508
EHSH(X)08P50A
508 BIV
EHSH(X)B08P50A
Cold water in
DHW out
Tank loading flow
Tank loading return
Bivalent flow
Bivalent return
Drain-Back flow
Drain-Back return
123 4 7 8
123 4756 8
Hydraulic

## Slide 49
516
EHSH(X)16P50A
516 BIV
EHSH(X)B16P50A
3.1.
123 4 7 8
123 4 756 8
Cold water in
DHW out
Tank loading flow
Tank loading return
Bivalent flow
Bivalent return
Drain-Back flow
Drain-Back return
Hydraulic

## Slide 50
Hydraulic
3.1.
Complete new Hydraulic
Compact build up
More flexibility due to changeable heating connection
New improved parts
  Flow sensor
  Mixing valves + Motor
  Pump
  Manual Air-purge
  New NTC-Sensor
Notes: Also cost down

## Slide 51
Hydraulic
3.1.
Isolation
Each part is marked with the a number
Mounting no. 2,3,4,…,9

## Slide 52
Hydraulic
3.1.
Front side
Pump
3UVB1
3UV DHW
tV
tR

## Slide 53
Hydraulic
3.1.
Rear side
Cold Water IN
DHW OUT
Safety valve
HC connection

## Slide 54
Hydraulic
3.1.
Rear side with PHE and ball valves (field supplied)
Flow Sensor
Pressure Sensor
Ball valves

## Slide 55
Hydraulic
3.1.
Filling and draining valve
Expansions vessel connection
Air purge

## Slide 56
Hydraulic
3.1.
Grundfos UPPM3 K
High efficiency pump
Automatic vent and safety valve integrated
Pump

## Slide 57
Hydraulic
3.1.
Changeable CH connections
Delivered top mounted
Counter-support with screwdriver
CH connection

## Slide 58
Hydraulic
3.1.
Manual Air vent
After 3UV DHW
Return PHE
Highest position

## Slide 59
Hydraulic
3.1.
Flow sensor
Huba DN 20
Flow downwards
Including Tr1 PTC Sensor

## Slide 60
Hydraulic
3.1.
Piping
connection for expansion vessel and pressure sensor
Filling and draining valve for the heating system
Notes: Must use for expansion vessle, otherwise not save

## Slide 61
Hydraulic
3.1.
Sensors
New improved NTC sensors
Improved sealing from outside
Corrosion resistance from inside

## Slide 62
Hydraulic
3.1.
Sensors
Only Tr1 is a PTC sensor

## Slide 63
Tv1,2
Tr2
Tr1
Flow
Tvbh
Hydraulic
3.1.
NTC Sensors
Tr1
Flow
Tr2
Tv1,2
Tvbh

## Slide 64
Hydraulic
3.1.
75sec from 0% - 100%  temperature control more precise
no metal spring inside  less force needed to change the position and no corrosion  higher reliability
3-Way-Valve
Notes: Ôld 180sec

## Slide 65
Hydraulic
3.1.
3UVB1 = Bypass-valve
  Switches between bypass and CH
3UV DHW = DHW
  Switches between DHW and CH

## Slide 66
Hydraulic
3.1.
Press
Press
To disconnect the motor from the valve both bottoms have to be pressed at the same time, than it is possible to turn the motor 45°C anti-clockwise
Turn
Notes: Lets try

## Slide 67
Hydraulic
3.1.
While disconnection the motor the valve turns 45°C (25%) anti-clockwise  this can create confusion of the position of the valve
The Motor is current less fixated  check with the manual the position of the valve
3UVB1 Motor can’t be wrongly mounted
3UV DHW can only be wrongly mounted if the isolation is missing

## Slide 68
Hydraulic
3.1.
Defrost
Tv1,2
Tr2
Tr1
Flow
Tvbh
Defrost signal
Pump on
Permanent control of Flow, Tr1 and Tvbh
Flow drops below 22l/min and/or Tr1 drops below 25°C  3UVB1 will drive to By-pass
Tvbh drops below 35°C 3UV DHW will drive to tank
Notes: Raoundabout 1 ,1 kw

## Slide 69
Hydraulic
3.1.
Charging thermal store (DHW preparation)
DHW demand
OU and Pump start
3UV DHW will drive to the tank
3UVB1 will drive to bypass
Operation will stop if DHW Set point is reached

## Slide 70
Hydraulic
3.1.
Heating operation only heat pump
Heating demand
OU and Pump start
3UV DHW will drive to CH
3UVB1 will drive to CH, under control of the flow (min 10l/min)
If necessary the 3UVB1 will bypass to keep the flow

## Slide 71
Hydraulic
3.1.
Heating operation BUH only
Heating demand
OU can’t run pump and BUH start
3UV DHW will drive to the tank
3UVB1 will drive to CH, under control of the flow (min 10l/min)
If necessary the 3UVB1 will bypass to keep the flow

## Slide 72
Hydraulic
3.1.
Heating operation with BUH/heating support
Heating demand
OU, pump and BUH start
3UV DHW will, controlled by temperature drive to the tank and CH
3UVB1 will drive to CH, under control of the flow (min 10l/min)
If necessary the 3UVB1 will bypass to keep the flow

## Slide 73
Hydraulic
3.1.
Cooling operation
Cooling demand
OU and pump start
3UV DHW will drive to CH
3UVB1 will, drive to CH under controll of the flow (14l/min)
If necessary the 3UVB1 will bypass to keep the flow
Parallel BOH operation is possible

## Slide 74
Hydraulic
3.1.
Bivalent charging
The bivalent heat exchanger is loading the tank from the bottom
Notes: 300l 6kw
500l 9kw max

## Slide 75
Hydraulic
3.1.
Drain-back operation
Depending on the flow and tank temperature the tank will be loaded at the highest, middle or lowest part
The return to the secondary heat source is taken from the bottom of the unit
Notes: Gelbes rohr nur bei 5xx

## Slide 76
Electronic
3.2
New ON/OFF buttom

## Slide 77
Electronic
3.2
CUI – Controller user interface
RoCon BM1 – ROTEX PCB
A1P – DAIKIN (BB) PCB
XAG1 – OU connection
RTX-EHS – Additional heat source PHC (Relias PCB)
XBUH1 – Additional heat source plug
RTX-AL 4 – RealTime PCB

## Slide 78
Electronic
3.2
Fast view on the main Temperatures, Operation mode and Error codes.
Rotary switch for fast exit to the common parameters
Text display with written parameters for easy understanding
CUI – Controller user interface

## Slide 79
Electronic
3.2
Clear text display
Configuration
Remote Parameter
Rotary switch
Info
Operation mode
Set Temp Day
Set Temp Night
Set Temp DHW
Rotary button with knob
DHW Install
Time Program
Exit / Reset
CUI – Controller user interface

## Slide 80
Electronic
3.2
Date
Status of refrigerant compressor
Status display
Time
Current flow temperature
Status heating circuit
Current outdoor temperature
Active operation mode
Status DHW
Current storage tank temperature
CUI – Controller user interface

## Slide 81
Electronic
3.2
Flashing: Heat pump demand
On: Compressor is running
No connection to the outdoor unit
Access right Expert active
Air purge active
Terminal function active
Frost protection active
“Party” temporary program active
“Away” temporary program active
“Holiday” temporary program active
“Vacation” temporary program active
Screed dry out active
CUI – Controller user interface

## Slide 82
Electronic
3.2
Normal Heating operation with Tvbh
Energy saving mode active
Mixed circuit with Tflow (M1)
Room sensor with Troom (U1)
Heating active
Cooling aktive
Inactive (no demand)
CUI – Controller user interface

## Slide 83
Electronic
3.2
Ambient temperature
Standby active
Reducing active
Heating active
Cooling active
Summer active
Automatic 1 active
Automatic 2 active
CUI – Controller user interface
Notes: Calculated ambeint temp

## Slide 84
Electronic
3.2
DHW temperature Tdhw1
DHW generation active
DHW generation inactive
CUI – Controller user interface

## Slide 85
Electronic
3.2
RoCon BM1 – ROTEX PCB

## Slide 86
Electronic
3.2
RoCon BM1 – ROTEX PCB
AUX – J3
The AUX outputs can be used for various different functions that can be parametrised.
The switch contact B-B1 is used, e.g. for connecting an external status display ("Cooling Mode Active") or as a changeover contact (heating/cooling) on the basic module of the underfloor heating regulation ROTEX RoCon UFH.
The switch-over contact A-A1-A2 can be used, for example, to control the heat generator in bivalent heating systems of ROTEX HPSU compact and oil or gas boiler.

## Slide 87
Electronic
3.2
RoCon BM1 – ROTEX PCB
CAN BUS– J13
The CAN BUS can be used for various different ROTEX RoCon Systems
M1 mixer module, U1 Room Controller or a Gateway
A maximum of 16/20 units can be connected
Each device has it’s own manual which have to be followed
4 cables are needed
  Grounding
  Power supply
  CAN in
  CAN out

## Slide 88
Electronic
3.2
RoCon BM1 – ROTEX PCB
EXT connection - J8
By connecting an external switching contact the operating mode of the ROTEX HPSU compact can be changed.
Changing the operating mode is only effective as long as the external switching contact is closed.
An operating mode activated by an external switch contact is shown on the controller by "EXT.", followed by the symbol of the operating mode.
A resistance is needed to choose the needed operation mode.
If the resistance is higher than Automatic 2 the input will be ignored

## Slide 89
Electronic
3.2
RoCon BM1 – ROTEX PCB
EBA (EDS) connection - J8
By connecting an External Demand Signal a Heating Signal can be generated via an external switch contact
The flow temperature is adjusted to the temperature that is set in the parameters [T-Flow Day].
The EDS has preference via the room thermostat.
In Cooling, Stand-by, Manual and Summer mode, the switching contact is not evaluated. In addition, the heating limits are not taken into consideration.
If additionally HZU is active and the storage tank is hot enough the pump will extract the energy out of the storage tank, the unit will remain off.

## Slide 90
Electronic
3.2
RoCon BM1 – ROTEX PCB
HT/NT connection - J8
If the outdoor unit is connected to a reduced tariff mains connection, the voltage-free switching contact S2S of the receiver which evaluates the low tariff input signal emitted by the electricity supply company (EVU) must be connected to the plug J8, connection EVU.
When the parameter [HT/NT Function] > 0 is set, certain system components are switched off during peak tariff times.
Notes: Current less otherviese strange sensors

## Slide 91
Electronic
3.2
RoCon BM1 – ROTEX PCB
Smart Grid connection - J8
Once the function is activated depending on the signal from the energy supply company, the heat pump is switched to Stand-by, Normal or an operating mode with higher temperatures.
As soon as the Smart Grid function is active, the HT/NT function is deactivated automatically. Depending on the value of the parameter [Mode SG] the heat pump operated in a different mode.

## Slide 92
Electronic
3.2
RoCon BM1 – ROTEX PCB
Update connection
Connection holes to update via DL-Plug
Only by trained service technicians

## Slide 93
Electronic
3.2
RoCon BM1 – ROTEX PCB
NO Dip has to be active
Only for PCB reset needed
M for MOD bus
GCU and A1 have E for E BUS
Notes: Currentless - right dipps up – push and hold buttom – put current on the unit – light flashes – light off – light on - release the buttom – currentless – dipps down – curren on – RESET DONE – Reset CUI
GCU and A1 have different internal E-BUS

## Slide 94
Electronic
3.2
A1P – DAIKIN (BB) PCB
Sensors

## Slide 95
Electronic
3.2
If you intend to run the internal heating pump continuously, it will need to be connected to the circuit board A1P, plug X17A, via a separate connection cable. (E1400132).
A1P – DAIKIN (BB) PCB

## Slide 96
Electronic
3.2
XAG1 – OU connection

## Slide 97
Electronic
3.2
Connection of an external heat generator or Rotex Backup Heater (BUxx)
RTX-EHS – Additional heat source PHC (Relias PCB)
XBUH1 – Additional heat source plug
Notes: Wires are now braced on.

## Slide 98
Electronic
3.2
It is possible to supply the BU9c with 400V or 230V (connected to BUL1-3)
  To reduce the stress to the relay
Additional heat source can be combined with a electrical heater element
  The heat supplied by the additional heat source must be added to storage tank water, either direct to the pressure less tank or via BIV heat exchanger
Demand to the additional heat generator is triggered by an relay on the PCB, the electrical connection can be done in different ways.
  With a potential-free contact or
  Only with power supply
RTX-EHS – Additional heat source PHC (Relias PCB)
XBUH1 – Additional heat source plug
Notes: 1. Draw 3 relais
3kw 1-2-3-1-2-3
6kw 12-23-31-12-23-31

## Slide 99
Electronic
3.2
RTX-AL 4 – RealTime PCB
Communication PCB between A1P and RoCon BM1
Tv1
In case of dummy Sensor values this PCB could be the cause
Notes: Relaiility changet to a 100% check

## Slide 100
Parameter
3.3
Overview
Water Pressure
T-HS
T-HS Setpoint
T-Outside
T-DHW
T-DHW Setpoint
T-Return
Flow Rate
T-HC
T-HC Setpoint
Status HS pump
Runtime Compressor
Runtime Pump
Mixer Position (3UVB1)
Qboh (for DHW)
Qchhp (for CH)
Qsc
Qch
QWP (produced)
Qdhw
HS type
Sw Nr. B1/U1
Sw Nr. Controller
Sw Nr RTX RT
General information
Notes: HS = Heatsource
HC = Heat ciruit

## Slide 101
Parameter
3.3
Overview
Mode
Pump

## Slide 102
Parameter
3.3
Overview
Ext
EHS
Notes: Can‘t check the system while LT on
EHS 3kw heating 6kw dhw 9 kw buh

## Slide 103
Parameter
3.3
Overview
RT
BPV

## Slide 104
Parameter
3.3
Overview
TV
TVBH
TR
Tdhw
TA
V
Notes: Ta at the moment

## Slide 105
Parameter
3.3
Overview
TVBH2
TR2
Tdhw2
Tliq2
TA2
quiet

## Slide 106
Parameter
3.3
Sw Nr. Controller
Sw Nr. B1/U1
Overview

## Slide 107
Parameter
3.3
Standby
Reducing
Heating
Cooling
Summer
Automatic 1
Automatic 2
Operation mode
The current operating mode is indicated by the related symbol in the standard display.
In Standby Energy Saving mode can be activated if:
  Additional Ambient sensor is connected, active and above 8°C
  No heating demand and no connected HC is on Frost protection
  Unit is powered for at least 5 min

## Slide 108
Parameter
3.3
Room set point temperature DAY
T-Room1 Setpoint
T-Room2 Setpoint
T-Room3 Setpoint
3 different temperature set points for the according timeframe
For heating and cooling
The set point is a value which is needed for the calculation of the LWT

## Slide 109
Parameter
3.3
Room set point temperature DAY
Notes: explain

## Slide 110
Parameter
3.3
Room set point temperature Night
T-Reduced
T-Absence

## Slide 111
Parameter
3.3
DHW set point temperature
T-DHW Setpoint 1
T-DHW Setpoint 2
T-DHW Setpoint 3
3 different temperature set points for the according timeframe

## Slide 112
Parameter
3.3
DHW Intallation
1x Hot Water
Hyst HP
Timer BOH
Notes: 1x HOT water = einmal ww sofort
Hysst = temp die ww sinken darf

## Slide 113
Parameter
3.3
Time program
Party
Away
Notes: Party wird angehängt away sofort

## Slide 114
Parameter
3.3
Automatic 1 = 06:00-20:00
Party mode = 2h
0:00 06:00 20:00 21:00 22:00 23:00 24:00
0:00 06:00 20:00 21:00 22:00 23:00 24:00
0:00 06:00 20:00 21:00 22:00 23:00 24:00
No Party
Party aktiv before 20:00
Party aktiv at 21:00
Example

## Slide 115
Vacation
Holiday (Sunday)
Parameter
3.3
Time program

## Slide 116
Parameter
3.3
Time program
HC Program1
HC Program2
DHW Program1
DHW Program2
Circulation Time

## Slide 117
Parameter
3.3
Time program
HC Program1
HC Program2
DHW Program1
Example:
DHW Program2
Circulation Time
06:00 -> 08:30
09:00 -> 15:00
15:00 -> 22:30
T-Room1 Setpoint = 20°C
T-Room 2 Setpoint = 25°C
T-Room 3 Setpoint = 18°C
T-Reduced = 15°C
0:00 06:00 08:30 9:00 15:00 22:30 24:00
18°
15°
20°
25°

## Slide 118
Parameter
3.3
Configuration
Setup
System Configuration
HC Configuration
DHW Configuration

## Slide 119
Parameter
3.3
Configuration
Setup
System Configuration
HC Configuration
DHW Configuration

## Slide 120
Parameter
3.3
Configuration
Setup
System Configuration
HC Configuration
DHW Configuration

## Slide 121
Parameter
3.3
Configuration
Setup
System Configuration
HC Configuration
DHW Configuration
Notes: Mixer confused if wrong set

## Slide 122
Parameter
3.3
Configuration
Setup
System Configuration
HC Configuration
DHW Configuration
Rod

## Slide 123
Parameter
3.3
Heating support (HZU)
If the heating support function (parameter [HZU] = On) is activated, the energy in the ROTEX HPSU compact integrated storage tank is used to take over the heating function.
At a sufficiently high storage tank temperature, the heat pump (refrigerant circuit) remains out of use.
THZUmin = [T-DHWSetpoint] + parameter [TDiff-DHW CH ].
Switch-on condition:
Tdhw > THZUmin + 4 K and Tdhw > info parameter [T-HS Setpoint] + 1 K
Switch-off condition:
Tdhw < THZUmin or Tdhw < info parameter [T-HS Setpoint]
Notes: On board example

## Slide 124
Parameter
3.3
Configuration
Setup
System Configuration
HC Configuration
DHW Configuration
Notes: BACKUPHEATER

## Slide 125
Parameter
3.3
SMART GRID

## Slide 126
Parameter
3.3
SMART GRID
As soon as the function is activated by the parameter [SMART GRID] = 1, the heat pump is moved to an operating mode, depending on the signal from the energy supply company.

## Slide 127
Parameter
3.3
Configuration
Setup
System Configuration
HC Configuration
DHW Configuration

## Slide 128
Parameter
3.3
Configuration
Setup
System Configuration
HC Configuration
DHW Configuration

## Slide 129
Parameter
3.3
Interlink function
Main Zone
Additional Zone
Switching form heating to cooling
tMAIN + 0-50K

## Slide 130
Parameter
3.3
Configuration
Setup
System Configuration
HC Configuration
DHW Configuration

## Slide 131
Parameter
3.3
Configuration
Setup
System Configuration
HC Configuration
DHW Configuration

## Slide 132
Parameter
3.3
Configuration
Setup
System Configuration
HC Configuration
DHW Configuration

## Slide 133
Parameter
3.3
Configuration
Setup
System Configuration
HC Configuration
DHW Configuration

## Slide 134
Parameter
3.3
Configuration
Setup
System Configuration
HC Configuration
DHW Configuration
Notes: Power dhw better 6 kw in case of slow sensors no overheating

## Slide 135
Parameter
3.3
Configuration
Setup
System Configuration
HC Configuration
DHW Configuration
Notes: Mixing valve will evaluate
No overheaeting of ufh

## Slide 136
Parameter
3.3
Power BIV Example
HPSU tank is loaded to 65°C and HZU is permitted.
3000W are taken for CH. (Power BIV)
The additional heater (BIV or DB) is loading the tank with more than 3000W.
Tank temperature won’t change. (3000W out and 3000W in)
Heat pump won’t start.
The needed heating load for the house is 4000W
 The house will cool down
Notes: Maybe draw at the borad

## Slide 137
Parameter
3.3
Configuration
Setup
System Configuration
HC Configuration
DHW Configuration
Quite mode reduced the capacity to 55% and tests showed a reduction of 10dbA (for GBS)
Notes: Gqi 1-3 dba

## Slide 138
Parameter
3.3
Configuration
Setup
System Configuration
HC Configuration
DHW Configuration

## Slide 139
Parameter
3.3
Configuration
Setup
System Configuration
HC Configuration
DHW Configuration

## Slide 140
Parameter
3.3
Configuration
Setup
System Configuration
HC Configuration
DHW Configuration

## Slide 141
Parameter
3.3
Configuration
Setup
System Configuration
HC Configuration
DHW Configuration
Notes: Parameter Off: no delay Parameter Good: delay of two hours
Parameter Low: delay of half an hour Parameter Very good: delay of three hours
Parameter Normal: delay of one hour

## Slide 142
Parameter
3.3
Configuration
Setup
System Configuration
HC Configuration
DHW Configuration
Notes: e.g tag 22°C nach 18°C würde heizen

## Slide 143
Parameter
3.3
Configuration
Setup
System Configuration
HC Configuration
DHW Configuration

## Slide 144
Parameter
3.3
Configuration
Setup
System Configuration
HC Configuration
DHW Configuration

## Slide 145
Parameter
3.3
Cooling
If the ambient temperature below 4°C the unit changes automatically to heating.
T_H/K Umschaltung (changeover) is reached unit changes to cooling, if the ambient temperature is min 2K below the unit changes back to the previous operation mode.

## Slide 146
Parameter
3.3
Configuration
Setup
System Configuration
HC Configuration
DHW Configuration

## Slide 147
Parameter
3.3
Special Level

## Slide 148
4. Commissioning
DAIKIN Altherma with integrated solar unit

## Slide 149
Title - Top secret/Secret/Internal use only/Public
149
Commissioning and Installation
4.
Outdoor Unit
Indoor Unit

## Slide 150
Installation OU
4.1
When installing the outdoor unit, the following points should be considered:
Is the unit safely situated
Can the unit be safely maintained
Is there sufficient room to remove components
Is there sufficient space to clean the outdoor unit heat exchanger
Is there adequate air flow available around the unit
Is there a requirement for a snow canopy
Is the discharge air route acceptable, no noisance towards neighbours
Is operational noise a problem to consider, is it under a bedroom window
Is drainage required on the outdoor unit
Prevailing wind

## Slide 151
4.1
We expect the installation of the equipment to comply with the installation instructions.
With this in mind, we also expect the outdoor unit not to be mounted directly onto the floor. i.e. the unit to be mounted on a wall bracket, or some form of elevated feet with all drain holes free.
 Minimum gap of 150mm required.
  Minimum 300 mm is recommended. For Scandinavian countries 500 mm due to snow & ice.
If the drain holes of the outdoor unit are covered by a mounting base or by floor surface, raise the unit in order to provide a free space of more than 150mm under the outdoor unit.
NOTE:
Installation OU

## Slide 152
4.1
Installation OU
a Baffle plate
b Prevailing wind direction
c Air outlet
a Snow cover or shed
b Pedestal
c Prevailing wind direction
d Air outlet
Install the outdoor unit in a way to prevent it from falling over.
Install the unit in a way so snow will NOT affect the unit.
Install a baffle plate when the air outlet is
exposed to wind.

## Slide 153
4.1
Installation OU
No drip tray under heat exchanger (free hanging coil)
No leaf guard to the side
New front grill to help prevent ice build up
New easy to install feet

## Slide 154
4.1
Installation OU
Mount feet first,
then mount unit to the back feet then secure the front feet

## Slide 155
4.1
Installation OU
EKFT008CA U-beams
Wall bracket mounting
Floor mounting
100mm
Fix the U-beams to the adequate support, fix rear unit feet, lift the unit to the support appropriately.
(continued on next slide)
Please use adequate health and safety protection - gloves

## Slide 156
4.1
Installation OU
Slide unit into rear feet already fixed to the U-beam, fix the front support feet and discard protective cardboard material
Please use adequate health and safety protection - gloves

## Slide 157
4.1
Installation OU
On selection of outdoor unit location, please ensure the location does NOT permit any re-circulation of the outdoor airflow.
Please allow for as much space around the outdoor unit as possible.
Minimum space for air passage
Wall height on air outlet side=less than 1200mm

## Slide 158
4.1
Installation OU
1 Baffle plate
2 Strong wind
3 Discharge air
Install a baffle plate when the air outlet is
exposed to wind.
1 Construct a large canopy.
2 Construct a pedestal.
Install the unit high enough
off the ground to prevent
burying in snow.
3 Strong wind
4 Discharge air without re-circulation
Install the outdoor unit in a way to prevent it from falling over.

## Slide 159
4.1
Installation OU
Install the outdoor temperature sensor (mounting kit is inside the accesory bag).
BEFORE
AFTER

## Slide 160
4.1
Installation OU
The unit should never be installed in a sound sensitive area (i.e. - a bedroom)
Vibration consideration of the water pump may need to be considered
The space around the unit is adequate for servicing
The space around the unit allows for sufficient air circulation
There is a provision for condensate drain (only for EHBX models) and pressure relief valve blow-off for all models
In case of wall hung indoor unit, the installation surface must be a flat and vertical wall capable of supporting the operating weight of the unit
All piping lengths and distances have been taken into consideration

## Slide 161
4.1
Installation OU
Electrical connection

## Slide 162
4.2
Installation IU
General rules for installation
The ground must be flat and level.
The ground load-bearing capacity must be at least 1050 kg/m²
Set-up in a explosion-risk environment is not permitted
The electronic control system must not be subjected to atmospheric factors under any circumstances.
The storage tank must not be exposed to continuous direct solar radiation, since the UV radiation and weather-influences will damage the plastic.
The ROTEX HPSU compact must be installed in a manner protected from frost.
The feed flow temperature of the external heater should be limited to max. 95 °C.
There is a danger of scalding at hot water temperatures over 60 °C. This is possible, when solar energy is used, with a connected external heating device, when the Legionella protection is activated or when the domestic hot water target temperature is set higher than 60 °C.  Install a scald protection

## Slide 163
4.2
Installation IU
Make sure that the supply company does not provide corrosive domestic water.
  Suitable water treatment may be required.
  Avoid damages caused by deposits and corrosion: Observe the relevant regulations of technology to prevent creation of corrosion products and deposits. Minimum requirements regarding the quality of filling and supplementary water:
    Water hardness (calcium and magnesium, calculated as calcium carbonate): ≤ 3 mmol/l
    Conductivity: ≤ 1500 (ideal ≤ 100) μS/cm
    Chloride: ≤ 250 mg/l
    Sulphate: ≤ 250 mg/l
    pH value (heating water): 6,5 - 8,5
If the ROTEX HPSU compact is connected to a heating system with steel pipes, radiators or non-diffusion-proof floor heating pipes, slurry and swarf could enter the hot water storage tank and cause blockages, local overheating or corrosion.
  Flush the feed pipes before filling the heat exchanger.
  Rinse out the heat distribution network (in the existing heating system).
  Install the dirt filter or sludge separator into the heating return flow
General rules for installation

## Slide 164
4.2
Installation IU
Bag of accessories
Notes: Abdeckungen wurden überarbeitet
Zange auch für ufh

## Slide 165
4.2
Installation IU
Installing the unit

## Slide 166
4.2
Installation IU
Installing the unit
Front
Back
All 4 positions can be used to carry the unit

## Slide 167
4.2
Installation IU
Installing the unit

## Slide 168
4.2
Installation IU
Installing optional electrical heating element

## Slide 169
4.2
Installation IU
Connecting Hydraulics
The connections for the heating feed and return flow can be directed out of the unit upwards or downwards in order to adapt to the on-site conditions in the most optimum manner.

## Slide 170
4.2
Installation IU
Connecting Hydraulics
In case of using the upwards connection the top cover has to be cut.
In case of using flexible connection they have to be fixed just before the unit.

## Slide 171
4.2
Installation IU
Filling the System
IT IS REQUIRED TO FILL ALL PIPE HEAT EXCHANGERS FIRST
Uplift force!
Therefrore it could be necessary to force the valves in middle positon.
Connect the drain hose to the connection piece for the safety overflow

## Slide 172
4.2
Installation IU
Venting the System manual

## Slide 173
4.2
Installation IU
Start up the System
Requirements
The ROTEX HPSU compact is fully connected.
The refrigerant system is dehumidified and filled with the specified amount of coolant.
The heating and hot water systems are filled and charged at the right pressure (see chapter 7.4).
The storage tank is filled up to the overflow (see chapter 7.3).
Optional accessories have been mounted on and connected up.
The control valves of the heating system are open.

## Slide 174
4.2
Installation IU
Air purge function
By activation the Air purge the HPSU will start in a defined sequence program of the integrated heat circulation pump and various settings for the 3-way valves.
Existing air can leak from the automatic venting valve at the integrated circulation pump.
Make sure the valve is open.
This function does not replace the correct venting of the heating system.
Monitor the pressure of the heating system
The complete procedure of pump and valves is shown in a precise workflow in the manual.

## Slide 175
4.2
Installation IU
Start up the System
Follow the Checklist

## Slide 176
4.2
Installation IU
Start up the System
If the storage temperature fall below a certain minimum value, the safety settings of the ROTEX HPSU prevent the operation of the heat pump in case of low external temperatures:
Ambient temperature ≤ -2°C, minimum storage temperature = 30°C
Ambient temperature ≤ 12°C , minimum storage temperature = 23°C
The backup heater is switched automatically on to reach the temperatures
Without the backup heater the water must be heated with an external heat source
To avoid any delay at the commissioning start first with the IU and start the backup heater with 9kW. Afterwards the OU commissioning can start with a heated up tank
Notes: One day --- switch back

## Slide 177
4.2
Installation IU
Screed dry-out program
The screed program to dry out of the UFH, should be adapted to the system.
Factory settings are the same as in GCU/A1.

## Slide 178
4.2
Installation IU
Screed dry-out program
When this function is activated the equilibrium temperature is raised to 25°C. The immersion heater is therefore allowed to run always parallel up to an ambient temperature of 25° C.
Only units with 11, 14, 16 KW can still run parallel up to 35°C ambient temperature
Interlink and Room thermostat function must be set to OFF.
The program will start the next day after setting at 0:00
When active all other influence will be deactivated and the unit will work on the fixed set flow
After the screed program is finished the until will switch back to previous operation mode.
The Interlink and Room thermostat function must be activated again an the heating curve must be set.

## Slide 179
5. Troubleshooting
DAIKIN Altherma with integrated solar unit

## Slide 180
Title - Top secret/Secret/Internal use only/Public
180
Troubleshooting
5.
Overview
DAIKIN Error codes
ROTEX Error codes

## Slide 181
Title - Top secret/Secret/Internal use only/Public
181
Overview
5.1
Fault code
Fault massage
Location
BUS address
Fault code
Location
BUS address

## Slide 182
Title - Top secret/Secret/Internal use only/Public
182
Overview
5.1
Read out protocol

## Slide 183
Title - Top secret/Secret/Internal use only/Public
183
DAIKIN Error codes
5.2

## Slide 184
Title - Top secret/Secret/Internal use only/Public
184
DAIKIN Error codes
5.2

## Slide 185
Title - Top secret/Secret/Internal use only/Public
185
DAIKIN Error codes
5.2

## Slide 186
Title - Top secret/Secret/Internal use only/Public
186
DAIKIN Error codes
5.2

## Slide 187
Title - Top secret/Secret/Internal use only/Public
187
DAIKIN Error codes
5.2

## Slide 188
Title - Top secret/Secret/Internal use only/Public
188
DAIKIN Error codes
5.2

## Slide 189
Title - Top secret/Secret/Internal use only/Public
189
DAIKIN Error codes
5.2

## Slide 190
Title - Top secret/Secret/Internal use only/Public
190
DAIKIN Error codes
5.2

## Slide 191
Title - Top secret/Secret/Internal use only/Public
191
DAIKIN Error codes
5.2

## Slide 192
Title - Top secret/Secret/Internal use only/Public
192
DAIKIN Error codes
5.2

## Slide 193
Title - Top secret/Secret/Internal use only/Public
193
DAIKIN Error codes
5.2

## Slide 194
Title - Top secret/Secret/Internal use only/Public
194
DAIKIN Error codes
5.2

## Slide 195
Title - Top secret/Secret/Internal use only/Public
195
ROTEX Error codes
5.3

## Slide 196
Title - Top secret/Secret/Internal use only/Public
196
ROTEX Error codes
5.3

## Slide 197
Title - Top secret/Secret/Internal use only/Public
197
ROTEX Error codes
5.3

## Slide 198
6. What should have been said
DAIKIN Altherma with integrated solar unit

## Slide 199
Title - Top secret/Secret/Internal use only/Public
199
What should have been said
6.
The error code protocol has been split up to end-user and expert mode.
  Warnings like (E9004/E198…) are only visible in expert mode.
  E9031/L5 and E9008/A5 wont be written in the protocol if they are just warnings. But Displayed while they’re created.
For next software 03B (CUI) L5,CO,7H and A5 won’t be displayed if they are not blocking
The ambient sensor of the OU can show temperatures till -44,9°C (before only -20°C)
Some parameters have been moved from End-user to Expert or from Expert to Service